**Old Woman Creek (OWC) NERR Meteorological Metadata**

**January – December 2020**

**Latest Update:** 08/23/2022

**I. Data Set and Research Descriptors**

1. **Principal investigator(s) and contact persons –**

Sebastian Mejia, Monitoring/Stewardship Coordinator

Sebastian.mejia@dnr.ohio.gov

Address:

Old Woman Creek NERR

2514 Cleveland Road East

Huron, Ohio 44839-9724

Phone: (419) 433-4601

**2) Entry verification –**

Data are uploaded from the CR1000 data logger via a RS-232 cable connected to a laptop (with a Windows 7 or newer operating system). Files are exported from LoggerNet in a comma-delimited format and uploaded to the CDMO where they undergo automated primary QAQC and become part of the CDMO’s online provisional database. During primary QAQC, data are flagged if they are missing or out of sensor range. The edited file is then returned to the Reserve where it is opened in Microsoft Excel and processed using the CDMO’s NERRQAQC Excel macro. The macro inserts station codes, creates metadata worksheets for flagged data and summary statistics, and graphs the data for review. It allows the user to apply QAQC flags and codes to the data, append files, and export the resulting data file to the CDMO for tertiary QAQC and assimilation into the CDMO’s authoritative online database. For more information on QAQC flags and QAQC codes, see Sections 11 and 12.

Sebastian Mejia is responsible for data management.

**3) Research objectives –**

The objective of this work is to record weather data over a long period of time for Old Woman Creek to capture long-term trends and seasonal variability in weather conditions. Weather conditions can be related to long-term trends and seasonal variability in estuary water quality. An added function is to provide the weather data so that researchers can examine the impact of changing weather conditions on the ecology of the estuary. Weather information is critical when studying the estuary because the estuary is a storm-driven system and the source of water in the estuary is a function of both storm activity in the watershed and on the lake proper.

**4) Research methods –**

Campbell Scientific data telemetry equipment (Sutron Sat-Link2 transmitter) was installed at this station on 07/19/2006 and transmits data to the NOAA GOES satellite, NESDIS ID #3B017310. The transmissions are scheduled hourly and contain four (4) data sets reflecting fifteen-minute data sampling intervals. The time zone for Local Standard Time is Eastern Standard Time. Upon receipt by the CDMO, the data undergo the same automated primary QAQC process detailed in Section 2 above. The “real-time” telemetry data become part of the provisional dataset until undergoing secondary and tertiary QAQC and assimilation in the CDMO’s authoritative online database. Provisional and authoritative data are available at https://cdmo.baruch.sc.edu.

The Wind Sentry, temperature and relative humidity sensor, barometric pressure sensor and the LiCor PAR sensor are located on a 10-meter tower following the descriptions outlined in the CDMO Manual V 4.0. The tipping bucket rain gauge is located about 2-3 meters southeast of the tower. The sensors are wired to the CR1000 following the protocol in the CDMO Manual. A new CR1000 data logger was installed on 5 September 2013 (re-calibrated 28 September 2018). New software was installed on 15 January 2014 at 15:30. The new software was altered by Mike Mensinger to include the new bp offset value (522), because Old Woman Creek is 604 feet above sea level.

Data collection information:

The 15-minute Data are collected in the following formats for the **CR1000**:

Averages from 5-second data:

Air Temperature (°C), Relative Humidity (%), Barometric Pressure (mb), Wind Speed (m/s), Wind Direction (degrees), Battery Voltage (volts)

Maximum and Minimum Air Temperature (°C) and their times from 5-second data (these data are available from the Reserve)

Maximum Wind Speed (m/s) and time from 5-second data

Wind Direction Standard Deviation (degrees)

Totals:

Precipitation (mm), PAR (millimoles/m2), and Cumulative Precipitation (mm) (Cumulative precipitation is no longer available via export from the CDMO. Please contact the Reserve or the CDMO for more information or to obtain these data.)

Calibration information:

Once a month, the sensors on the weather station are inspected for damage and cleaned, if necessary.

Calibration frequency is as follows:

- Temperature/Humidity- yearly recalibration

- Rain Gauge- yearly recalibration

- Wind Speed/Direction- every 2 years

- Barometric Pressure- every 2 years recalibration

- PAR- every 2 years recalibration

- CR1000-every 5 years (required beginning 2014, one year initial grace period)

Data quality checks:

Ongoing checks of data quality include comparing data from nearby weather stations with OWC weather data approximately weekly. Precipitation data are also compared to data collected by a manual and digital gauge on site and other local rain gauge monitors (OH-ER-11, OH-ER-18) through [CoCoRaHs](https://www.cocorahs.org/ViewData/StationPrecipSummary.aspx). When the data are downloaded monthly, a handheld Kestrel 4000 is used to provide a general check of the sensors.

**5) Site location and character –**

The Old Woman Creek State Nature Preserve and National Estuarine Research Reserve is located on the southern shore of Lake Erie east of the City of Huron, Ohio. The reserve lies within the Lake Erie Biogeographic Region. Old Woman Creek drains a primarily row-crop agricultural watershed, with corn, soybeans, and winter wheat being the most predominant crops. The weather station is located within the boundaries of the reserve, due east of the parking lot at the Michael Dewine Center for Coastal Research in a field that is maintained in early succession. This ensures that no tall vegetation will interfere with the weather station. The tower is located within an approximately 5-m square fenced (6-foot chain link fencing) enclosure with a gravel base. The coordinates of the station are 41˚ 22’40” N and 82˚ 30’ 29”W. Wind speed and wind direction sensors are atop a 10 meter tower, while the PAR sensor is located off of the south-west edge of the tower at approximately 3 meters in height. The temperature/ RH sensor is located off the north-east edge of the tower at approximately 2.3 meters in height. The barometric pressure sensor is located within the instrument box on the tower at approximately 2 meters in height. The sensor is vented to the outside through a hole in the bottom of the instrument box. The heated tipping rain gauge is located about 2-3 meters southeast of the tower on a platform about 1 meter above the ground. The weather station is located within 1 kilometer of three of the SWMP water quality data logger sites (WM, OL, and DR) and within 5 kilometers of the fourth water quality data logger site (BR). The site is 604 feet above sea level.

SWMP Station Timeline

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Station Code | SWMP Status | Station Name | Location | Active Dates | Reason Decommissioned | Notes |
| owcowmet | P | Old Woman Creek | 41˚ 22’40” N  82˚ 30’ 29”W | 2002- present | NA | NA |

**6) Data collection period –**

Weather data were collected starting 02 December (13:30 EST) 2019 through 31 January 2021; reported data begin 1 January (00:00 EST) 2020 and end 31 December (23:45 EST) 2020.

|  |  |  |
| --- | --- | --- |
| File Start Date and Time | File End Date and time | Download Date |
| 12/02/2019 13:30 | 01/02/2020 08:30 | 01/02/2020 |
| 01/02/2020 08:45 | 02/02/2020 08:30 | 02/03/2020 |
| 02/02/2020 08:45 | 03/02/2020 09:30 | 03/02/2020 |
| 03/02/2020 09:45 | 04/02/2020 08:30 | 04/02/2020 |
| 04/02/2020 08:45 | 05/01/2020 15:15 | 05/01/2020 |
| 05/01/2020 15:30 | 06/01/2020 11:45 | 06/02/2020 |
| 06/01/2020 12:00 | 06/25/2020 08:30\* | 06/25/2020 |
| 06/25/2020 10:45 | 08/03/2020 11:30 | 08/03/2020 |
| 08/03/2020 11:45 | 09/03/2020 13:00 | 09/03/2020 |
| 09/03/2020 13:15 | 10/01/2020 09:15 | 10/01/2020 |
| 10/01/2020 09:30\*\* | 11/03/2020 12:45\*\*\* | 11/03/2020 |
| 11/03/2020 16:30 | 11/04/2020 09:15 | 11/04/2020 |
| 11/04/2020 09:30 | 11/09/2020 10:15 | 11/09/2020 |
| 11/09/2020 14:15 | 12/02/2020 14:30 | 12/03/2020 |
| 12/02/2020 14:45 | 01/04/2021 11:45 | 01/04/2021 |

\*Start of missing data due to station power down for sensor swap and maintenance.

\*\*Accidental program reload led to CR1000 data loss. Data recovered via telemetry.

\*\*\*Start of intermittent gaps of missing data due to CR1000 and TX312 malfunctioning.

**7) Distribution –**

NOAA retains the right to analyze, synthesize and publish summaries of the NERRS System-wide Monitoring Program data.  The OWC Research Coordinator (RC) and the NERRS retain the right to be fully credited for having collected and processed the data.  Following academic courtesy standards, the RC or Manager at the NERR site where the data were collected should be contacted and fully acknowledged in any subsequent publications in which any part of the data are used.

The data set enclosed within this package/transmission is only as good as the quality assurance and quality control procedures outlined by the enclosed metadata reporting statement.  The user bears all responsibility for its subsequent use/misuse in any further analyses or comparisons.  The Federal government and the State of Ohio do not assume liability to the Recipient or third persons, nor will the Federal government or State of Ohio reimburse or indemnify the Recipient for its liability due to any losses resulting in any way from the use of this data.

Requested citation format:

NOAA National Estuarine Research Reserve System (NERRS). System-wide Monitoring Program. Data accessed from the NOAA NERRS Centralized Data Management Office website: <http://www.nerrsdata.org/>; *accessed* 12 October 2020.

NERR meteorological data and metadata can be obtained from the Research Coordinator at the individual NERR site (please see Principal Investigators and Contact Persons), from the Data Manager at the Centralized Data Management Office (please see personnel directory under the general information link on the CDMO home page) and online at the CDMO home page [www.nerrsdata.org](http://www.nerrsdata.org).  Data are available in comma delimited format.

**8) Associated researchers and projects –**

As part of the SWMP long-term monitoring program, OWC NERR also collects 15-minute water quality data along with monthly grab samples and diel sampling for nutrient data at four stations within the estuary. 15-minute water level data are collected at the DR water quality station and adjacent to the WM water quality station. These data may be correlated with this meteorological dataset. Three of the four current SWMP water quality stations (WM, OL, DR) and one former station (SU) are located within 1 kilometer of this weather station; the fourth current station (BR) is located within 5 kilometers and has a USGS water gauge adjacent to it. The four sites were established to determine the role of the estuary in mitigating storm flow through the system and the impact of Lake Erie on the estuary. These data are available at [www.nerrsdata.org](http://www.nerrsdata.org). Periodic vegetation and habitat data and maps also exist and are available from the reserve.

**II. Physical Structure Descriptors**

**9) Sensor specifications –**

Parameter: Temperature

Units: degrees Celsius

Sensor type: PT100 RTD, IEC 751 1/3 Class B, with calibrated signal conditioning

Model: Rotronic HC2-S3 Temperature and Relative Humidity Probe

Operating Temperature: -40°C to +60°C

Range: -40°C to +60°C

Accuracy: +0.1°C at 23°C

Serial Number 61115231 (Retired)

Date of Last Calibration: 09/26/2018

Dates of Sensor Use: 10/19/2018 (08:15) – 07/01/2019 (15:30)

Serial Number 60749921(Retired)

Date of Last Calibration: 05/23/2019

Dates of Sensor Use: 07/01/2019 (16:15) – 06/25/2020 (08:30)

Sensor type: PT100 RTD, Class A, with calibrated signal conditioning

Model: E+E Elektronik EE181 Temperature and Relative Humidity Probe

Operating Temperature: -40°C to +60°C

Range: -40°C to +60°C

Accuracy: ±0.2°C at 23°C

Serial Number 20021600052164

Date of Last Calibration: 01/16/2020

Dates of Sensor Use: 06/25/2020 (10:45) – current as of 12/31/2020

Parameter: Relative Humidity

Units: Percent

Sensor type: ROTRONIC® Hygromer IN-1

Model: Rotronic HC2-S3 Temperature and Relative Humidity Probe

Range: 0-100% non-condensing

Accuracy at 23˚C: +0.8% RH with standard configuration settings

Temperature dependence of RH measurement +/- 3% (-40 to 60C)

Serial Number 61115231 (Retired)

Date of Last Calibration: 09/26/2018

Dates of Sensor Use: 10/19/2018 (08:15) – 07/01/2019 (15:30)

Serial Number 60749921(Retired)

Date of Last Calibration: 05/23/2019

Dates of Sensor Use: 07/01/2019 (16:15) – 06/25/2020 (08:30)

Sensor type: HC101

Model: E+E Elektronik EE181 Temperature and Relative Humidity Probe

Range: 0-100% non-condensing

Accuracy:

–15 to 40 °C: ≤90% RH ± (1.3 + 0.003 • RH reading) % RH

–15 to 40 °C: >90% RH ± 2.3% RH

–25 to 60 °C: ± (1.4 + 0.01 • RH reading) % RH

–40 to 60 °C: ± (1.5 + 0.015 • RH reading) % RH

Serial Number 20021600052164

Date of Last Calibration: 01/16/2020

Dates of Sensor Use: 06/25/2020 (10:45) – current as of 12/31/2020

Parameter: Barometric Pressure

Units: millibars (mb)

Sensor type Vaisala Barocap© silicon capacitive pressure sensor

Model # Vaisala PTB110 Barometer (PTB110 1B0CA)

Temperature Range: -40° to + 60°C

Accuracy: + 0.3 mb at 20°C; + 0.6mb at 0°C to 40°C; + 1mb at –20°C to 45°C; + 1.5mb at –40°C to 60°C

Stability: + 0.1 mb per year

Serial Number J2060017

Date of Last Calibration: 08/29/2017

Dates of Sensor Use: 09/13/2017 (16:15) – 07/01/2019 (15:30)

Serial Number G4870077

Date of Last Calibration: 05/29/2019

Dates of Sensor Use: 07/01/2019 (16:15) – current as of 12/31/2020

Parameter: Wind speed

Units: meters per second (m/s)

Sensor type: 18 cm diameter 4-blade helicoids propeller molded of polypropylene

Model: R.M. Young Model 05103 Wind Monitor

Range: 0-60 m/s (134 mph); gust survival 100 m/s (220 mph)

Accuracy: +/- 0.3 m/s

Serial Number WM75736

Date of last calibration: 06/25/2020 (serviced nose cone installed), previous calibration 05/30/2018

Dates of sensor use: 11/02/2006 – current as of 12/31/2020

Parameter: Wind direction

Units: degrees

Sensor type: balanced vane, 38 cm turning radius

Model: R.M. Young Model 05103 Wind Monitor

Range: 3600 mechanical, 3550 electrical (50 open)

Accuracy: + 5%

Serial Number WM75736

Date of last calibration: 06/25/2020 (serviced nose cone installed), previous calibration 05/30/2018

Dates of sensor use: 11/02/2006 – current as of 12/31/2020

Parameter: PAR (Photosynthetically Active Radiation)

Units: mmoles m-2 (total flux)

Sensor type: High stability silicon photovoltaic detector (blue enhanced)

Model: LiCor Quantum Sensor LI190SB

Light spectrum waveband: 400 to 700 nm

Temperature dependence: 0.15% per ˚C maximum

Stability: <+2% change over 1 year

Operating Temperature: -40° to +65° C; Humidity 0 to 100%

Sensitivity: typically, 5 µA per 1000 µmoles s-1 m-2

Serial Number Q49472 (Retired)

Multipliers: 1.1997

Date of Last Calibration: 03/10/2016

Dates of Sensor Use: 09/13/2017 (16:15) – 11/26/2019 (11:45)

Serial Number Q46576

Multipliers: 1.7996

Date of Last Calibration: 12/13/2017

Dates of Sensor Use: 11/26/2019 (12:15) – current as of 12/31/2020

Parameter: Precipitation (heated rain gauge – not functioning)

Units: millimeters (mm)

Sensor Tipping Bucket Rain Gauge

Model: Met One Model 385Heated Rain Gauge

Sensitivity: 0.2mm

Rainfall per tip: 0.01 inch

Operating range: Temperature: -20° to 50°C; Humidity: 0 to 100%

Accuracy: + 0.5% < 0.5 in./hr rate; + 2.0% < 3 in./hr rate

Serial Number A1415 (was misidentified as F5714 since at least 2013)

Date of Last Calibration: 01/15/2020, previous calibration 10/25/2018

Dates of Sensor Use: pre 04/01/2007 – current as of 12/31/2020

The Campbell Scientific CR1000 has two MB Flash EEPROM that is used to store the Operating System. Another 128 K Flash is used to store configuration settings. Four MB SRAM is used for program storage (16K), operating system use, and data storage. Data are downloaded from the CR1000 to a laptop via RS-232 cable using LoggerNet software.

CR1000 Serial Number 58337 (mislabeled as 57851 from 2013 – 2017), (Retired)

Date installed: 09/05/2013

Date calibrated: 08/22/2013

Date removed: 09/12/2018 14:45

CR1000 Serial Number 72109 (Retired)

Date installed: 09/12/2018 15:45

Date calibrated: 07/23/2018

Date removed: 10/18/2018 15:15

CR1000 Serial Number 58337

Date installed: 10/19/2018 08:30

Date calibrated: 09/28/2018

Date Removed: Current as of 12/31/2020

CR1000 Firmware Version (s): OS 26, updated when purchased but went back to OS26 on 11/28/2018; OS 32.05 as of 06/25/2020

CR1000 Program Version(s):

12/18/2017 (16:30) – 12/02/2019 (13:15): owcowmet\_5.5\_091317\_2.CR1

12/02/2019 (14:00) – 06/25/2020 (08:30): owcowmet\_5.5\_120219.CR1 (updated with new PAR multiplier)

06/25/2020 (10:45) – 11/09/2020 (10:15): owcowmet\_6.1.2\_062520.CR1

11/09/2020 (14:00) – current as of 12/31/2020: owcowmet\_6.1.2\_062520.110920.CR1

**10) Coded variable definitions -**

Sampling station: Sampling site code: Station code:

Old Woman Creek OW owcowmet

**11) QAQC flag definitions –**

QAQC flags provide documentation of the data and are applied to individual data points by insertion into the parameter’s associated flag column (header preceded by an F\_). During primary automated QAQC (performed by the CDMO), -5, -4, and -2 flags are applied automatically to indicate data that are above or below sensor range, or missing. All remaining data are then flagged 0, as passing initial QAQC checks. During secondary and tertiary QAQC 1, -3, and 5 flags may be used to note data as suspect, rejected due to QAQC, or corrected.

-5 Outside High Sensor Range

-4 Outside Low Sensor Range

-3 Data Rejected due to QAQC

-2 Missing Data

-1 Optional SWMP supported parameter

0 Passed Initial QAQC Checks

1 Suspect Data

2 *Open - reserved for later flag*

3 *Open - reserved for later flag*

4 Historical Data: Pre-Auto QAQC

5 Corrected Data

**12) QAQC code definitions** –

QAQC codes are used in conjunction with QAQC flags to provide further documentation of the data and are also applied by insertion into the associated flag column. There are three (3) different code categories, general, sensor, and comment. General errors document general problems with the CR1000/CR1000X, sensor errors are sensor specific, and comment codes are used to further document conditions or a problem with the data. Only one general or sensor error and one comment code can be applied to a particular data point, but some comment codes (marked with an \* below) can be applied to the entire record in the F\_Record column.

General Errors

GIM Instrument malfunction

GIT Instrument recording error, recovered telemetry data

GMC No instrument deployed due to maintenance/calibration

GMT Instrument maintenance

GPD Power down

GPF Power failure / Low battery

GPR Program reload

GQR Data rejected due to QA/QC checks

GSM See metadata

Sensor Errors

SDG Suspect due to sensor diagnostics

SIC Incorrect calibration constant, multiplier or offset

SIW Incorrect wiring

SMT Sensor maintenance

SNV Negative value

SOC Out of calibration

SQR Data rejected due to QAQC checks

SSD Sensor drift

SSN Not a number / unknown value

SSM Sensor malfunction

SSR Sensor removed

Comments

CAF Acceptable calibration/accuracy error of sensor

CCU Cause unknown

CDF Data appear to fit conditions

CML Snow melt from previous snowfall event

CRE\* Significant rain event

CSM\* See metadata

CVT\* Possible vandalism/tampering

CWE\* Significant weather event

**13) Other remarks/notes** –

General

Data are missing due to equipment or associated specific sensors not being deployed, equipment failure, time of maintenance or calibration of equipment, or repair/replacement of a sampling station platform. Any NANs in the dataset stand for “not a number” and are the result of low power, disconnected wires, or out of range readings. If additional information on missing data is needed, contact the Research Coordinator or Monitoring/Stewardship Coordinator at the reserve submitting the data.

Data recorded for all parameters (except for cumulative precipitation) at the midnight timestamp (00:00) are the 15-minute averages and totals for the 23:45-23:59 time period of the previous day. Cumulative precipitation data at the midnight timestamp (00:00) are the sum of raw (unrounded) precipitation data from 00:00 to 23:59 of the previous day. Summing each individual 15-minute total precipitation value from the same period will result in small differences from cumulative precipitation due to rounding. It is especially important to note how data at the midnight timestamp are recorded when using January 1st and December 31st data. **Note: Cumulative precipitation is no longer available via export from the CDMO. Please contact the Reserve or the CDMO for more information or to obtain these data.**

Maintenance

Total precipitation and cumulative precipitation were coded <0>[SMT](CSM) for rain gauge calibration that occurred on 01/15/2020 from 10:15 – 14:30. The rain gauge calibration was done offline and no precipitation data were recorded.

The tipping buckets were accidentally tipped during monthly maintenance on the following dates and time: 06/01/2020 11:45, 06/25/2020 13:30, Total precipitation and cumulative precipitation (through the end of the day) were corrected and flagged and coded <5>[SMT](CSM).

Temp/RH sensor and wind sensor nose cone were swapped on 06/25/2020 from 8:45 - 10:45, which necessitated powering down the weather station. A new program was uploaded for the 06/25/2020 10:45 timestamp, <3>[GPR](CSM).

Missing data

Missing data due to station power down for sensor exchange are flagged

<-2>[GPD](CSM) and include: 06/25/2020 8:45-10:30.

Intermittent data loss occurred beginning in October 2020 and continued until the end of the year most likely due to a faulty TX312 transmitter causing compiling problems with the CR1000. The F\_Record of affected timestamps with missing data <-2> [GIM]were marked {CSM}

Telemetry data were used to replace missing records from 10/01/2020 09:30 - 11/03/2020 16:15 that were overwritten with a logger program upload. There were multiple occasions of missing data from dropped transmissions (see above <-2> [GIM] {CSM}, most likely due to a faulty TX312 transmitter. Cumulative precipitation data are also missing from telemetry data files. All other records replaced with telemetry data are considered suspect, <1> [GIT] (CSM), including elevated nighttime PAR. Any erroneous data were rejected, <-3> [GIT] (CSM).

Data are missing 11/09/2020 10:30 – 14:00 due to a program upload error, <-2> [GPR] {CSM}.

Sensor Exchange

A program with the updated PAR multiplier was uploaded on 12/02/2019 between 13:30 and 14:00. It appears the PAR multiplier uploaded correctly; however, the CR1000 did not reset as expected with the program reload (record number and cumulative precipitation did not reset to 0). Data were rejected due to the upload since the 15- minute collection intervals may be missing 5-second readings. PAR data from 12/02/2019 14:15 through 06/25/2020 08:30 are coded with CSM, including suspect negative and elevated nighttime values). Although the data seem to be accurate and the new multiplier appears to have uploaded correctly in 2019, users should be aware that the program upload did not reset the CR1000 as expected and we cannot verify that the changes were made.

Precipitation

The gauge calibration was checked on 11/26/2019 12:05 and found to be out of calibration. Therefore, all precipitation data 11/26/2019 12:05 through 01/15/2020 10:00 were flagged as suspect <1> [SOC](CSM).

Following the program upload on 06/25/2020 10:45, cumulative precipitation values were doubled due to a programming error. All cumulative precipitation values are rejected when precipitation values were >0.0 following the program upload and continuing into 2021, <-3> (CSM). Cumulative precipitation data are not available for export, but are available from the reserve. If cumulative data were recorded during maintenance, they were corrected back to 0.0 when no precipitation occurred.

The electrical line that powers the heated precipitation gauge does not function. Precipitation data associated with snow events during these months are not likely to be accurate. Local [CoCoRaHs](https://www.cocorahs.org/ViewData/StationPrecipSummary.aspx) stations (OH-ER-18, OH-ER-11) were referenced for snowmelt. Snow occurred on the following dates and were coded as <0>(CSM), while dates and times snowmelt occurred flagged and coded as suspect, <1> [GSM](CML), unless another coding took precedence. Snowmelt may have occurred during the snowfall event or it may have been delayed depending on how quickly it melted. Flagging and coding of snowmelt for cumulative precipitation continues until the end of the day:

|  |  |
| --- | --- |
| **Snowfall Date(s)\*** | **Notes\*** |
| 12/31/2019 | ~1.27-1.91 cm |
| 1/5/2020 | < 0.635 cm |
| 1/17-18/2020 | ~5.08 cm of snow followed by freezing rain |
| 1/19-20/2020 | ~5.08 cm of snow |
| 2/4/2020 | Light snow (PM) |
| 2/5/2020 | Freezing rain (PM) |
| 2/6-8/2020 | Off and on snow; ~7.37 cm |
| 2/9-10/2020 | PM Snow into rain, then snowmelt and rain |
| 2/12-13/2020 | (PM) snow through (AM) ~5.08-6.35 cm and snowmelt |
| 2/15-16/2020 | Snowmelt |
| 2/17-18/2020 | Snowmelt and rain |
| 2/25/2020 | Rain and snow mix (PM) |
| 2/26/2020 | Light snow (AM) into heavy snow overnight (~7.62 cm) |
| 2/27-28/2020 | Light snow |
| 3/1-2/2020 | Snowmelt and rain |
| 04/10/2020 | Rain and hail (10:00-17:00)\*\* |
| 04/16/2020 | Snow (8:45-18:00) |
| 11/30-12/1/20 | Heavy Snow +15cm |
| 12/17/2020 | Snow |
| 12/24-25/20 | Snow\*\*\* |
| 12/29-31/20 | Light snow w/ little accumulation |

\*These dates reflect observed snowfall and snowmelt; however, users should be aware that snow loss due to sublimation may have occurred.

\*\*Hail may have clogged the gauge, these data are considered suspect, <1> (CSM)

\*\*\*Not recorded for total precipitation; instrument malfunction resulted in missing data.

PAR

Small negative PAR values are within range of the LI-COR sensor and are due to normal errors in the sensor and the CR1000 Datalogger. The Maximum signal noise error for the LI-COR sensor is +/- 2.214 mmoles/m2 over a 15-minute interval. These values are automatically flagged and coded as <1> (CAF). Negative values less than the maximum signal noise are rejected, <-3> [SNV] (CSM).

Elevated nighttime PAR data are flagged as <1> CSM if values are > 0.1 and < 2.214 mmoles/m2 and as <-3> CSM if values are >2.214 mmoles/m2.

Temperature/RH

Relative Humidity data greater than 100 are within range of the sensor accuracy of +/-3% and are flagged and coded as suspect, <1> (CAF). Values greater than 103 are rejected <-3>.

Air temperature and relative humidity data were rejected for QAQC checks, <-3> [SQR] (CSM) because of a high maximum air temperature reading(46oC) on 10/01/2020 09:15. Max and min air temperatures are not included in the data but are available from the reserve.

Wind data

Birds of various sizes and weights (e.g., bluebird, hawk) will occasionally sit on the wind sensor. These data are not flagged or coded.